## Sheet0
STATE LOAD DESPATCH CENTRE Madhya Pradesh Power Transmission Company Limited, Jabalpur
From Date: | 2025-10-04 |  |  | APPROVED OUTAGE LIST FOR DTD. 04.10.25
Control Area : | ALL | Circle : | ALL
S.NO. | APPLICATION DATE | REQ_ID | REQ TYPE | ELEMENT | SUBSTATION | CATEGORY TYPE | REASON FOR SHUT DOWN | PROPOSED START DATE & TIME | PROPOSED STOP DATE & TIME | Availing Officer Name & Mob. No. |  | REMARK
1 | 2025-10-03 12:03 | MR2510/0056 | Daily | 220KV_220 kV Adampur-Hoshangabad line | 220KV_ADAMPUR | NON-OCCM-MP | Defective Disc replacement work | 04-10-2025 09:00:00 | 14-10-2025 17:00:00 | Ankit Mehroliya | 9425804506 | ok, through sub ld
2 | 2025-10-03 12:55 | MR2510/0059 |  | 132KV_132KV Alot-Barod Line | 132KV_ALOT | NON-OCCM-MP | Line Maintenance work | 04-10-2025 10:00:00 | 04-10-2025 18:00:00 | Kamal Solanki | 9425805262 | sub ld
3 | 2025-10-03 14:13 | MR2510/0066 |  | 132KV_132 kV Anuppur-Dongrital Circuit | 220KV_ANUPPUR | NON-OCCM-MP | F/o disc stringing replacement & other line maint. | 04-10-2025 10:00:00 | 04-10-2025 17:00:00 | Jitendra Tiwari | 9425805298 | ok
4 | 2025-10-03 11:23 | MR2510/0053 |  | 220KV_220KV Main Bus section-l | 220KV_BARWAHA | NON-OCCM-MP | Shutdown taken on Hot point attending work | 04-10-2025 09:00:00 | 04-10-2025 15:00:00 | Er.Imran Beg | 9425805200 | APPROVED FOR 4 HRS.OSP 5 M/C TO BE RUN DURING S/D PERIOD.
5 | 2025-10-03 14:01 | MR2510/0063 |  | 132KV_132 KV Bina-Khurai Ckt-2 | 220KV_BINA | NON-OCCM-MP | For line maintenance work. | 04-10-2025 10:00:00 | 04-10-2025 18:00:00 | Sanjay Singh Thakur | 9425806936 | Deffered due to s/d on sagar 160MVA x-mer
6 | 2025-10-03 14:11 | MR2510/0065 |  | 220KV_220kV Chhatarpur-Ajaygarh (TBCB) Ckt. Ist Line | 220KV_CHATARPUR | NON-OCCM-MP | AH Tightening & other Line maintenance work | 04-10-2025 10:00:00 | 04-10-2025 18:00:00 | Manoj Kumar Tiwari | 9425804993 | ok
7 | 2025-10-02 11:21 | MR2510/0022 | Daily | 132KV_132kV Deolond - Beohari Ckt | 132KV_DEVLOND | NON-OCCM-MP | OPGW Work | 03-10-2025 07:00:00 | 30-10-2025 19:00:00 | G.L Sahu | 9425805102 | data availability confirmation required from communication
8 | 2025-10-02 11:19 | MR2510/0021 | Daily | 132KV_132kV Deolond - Jhinna ckt | 132KV_DEVLOND | NON-OCCM-MP | OPGW Work | 03-10-2025 07:00:00 | 30-10-2025 19:00:00 | G.L Sahu | 9425805102 | data availability confirmation required from communication
9 | 2025-10-03 16:16 | MR2510/0076 |  | 132KV_132KV Guna Bhonra Ckt. Ist | 220KV_GUNA | NON-OCCM-MP | DF/O replacement & other line maint. work | 04-10-2025 10:00:00 | 04-10-2025 17:00:00 | Akhilesh Singh | 8586865656 | sub ld
10 | 2025-10-01 09:35 | MR2510/0001 | Daily | 132KV_132 kV Jabalpur Bargi (MPPTCL) | 220KV_JABALPUR | NON-OCCM-MP | Installation of Joint Box at loc no 29/4 | 02-10-2025 08:00:00 | 04-10-2025 19:00:00 | Jitendra Tiwari | 9425805298 | ok
11 | 2025-10-03 16:31 | MR2510/0079 |  | 132KV_40mva EMCO X-MER | 132KV_KYMORE | NON-OCCM-MP | For repairing of bus isolators | 04-10-2025 10:00:00 | 04-10-2025 14:00:00 | RP Rawat | 7974696966 | o&m consent required
12 | 2025-10-03 15:19 | MR2510/0069 |  | 132KV_63 MVA Transformer -I BBL | 132KV_MANAWAR | NON-OCCM-MP | For post monsoon Maintenace work | 04-10-2025 10:00:00 | 04-10-2025 18:00:00 | Er. Kailash Morya | 9425813540 | sub ld
13 | 2025-10-03 15:20 | MR2510/0070 |  | 132KV_63 MVA Transformer -I BBL | 132KV_MANAWAR | NON-OCCM-MP | For post monsoon Maintenace work | 04-10-2025 10:00:00 | 04-10-2025 18:00:00 | Er. Kailash Morya | 9425813540 | sub ld
14 | 2025-10-03 11:43 | MR2510/0054 |  | 220KV_160MVA XMER-1 AREVA MAKE | 220KV_MANDIDEEP | NON-OCCM-MP | POST MONSOON MAINT. AND TESTING WORK | 04-10-2025 09:00:00 | 04-10-2025 18:00:00 | A.K. VERMA | 9425801324 | ok, through sub ld
15 | 2025-10-02 15:27 | MR2510/0050 | Continuous | 220KV_220/132 Kv 160MVA BHEL 3 X-mer | 220KV_NARSINGHPUR | NON-OCCM-MP | Replacement of CB,PI&Mainbus isolator erection | 03-10-2025 09:00:00 | 08-10-2025 17:00:00 | Dinesh Kumar Kushwaha | 9425182413 | Continuous
16 | 2025-10-03 16:29 | MR2510/0078 |  | 132KV_50 MVA BBL-make-Make Transformer | 132KV_ORCHHA | NON-OCCM-MP | Post mansoon maintenance | 04-10-2025 10:00:00 | 04-10-2025 16:00:00 | Pushpendra Kumar soni | 9425806398 | ok
17 | 2025-10-03 13:33 | MR2510/0061 |  | 220KV_200 MVA "X"-mer 220/132 KV CGP | 220KV_PANDHURNA | OCCM-MP | Leakage from Air leak detector/Cops relay installe | 04-10-2025 12:00:00 | 04-10-2025 15:00:00 | Sanjay Shende | 9425811447 | ok
18 | 2025-10-03 15:50 | MR2510/0074 |  | 132KV_40 MVA BHEL TRANSFORMER | 132KV_RAHATGARH | NON-OCCM-MP | PostMonsoon Maintenanace work | 04-10-2025 10:00:00 | 04-10-2025 17:00:00 | Bhupendra khawse | 9074588975 | o&m consent required
19 | 2025-10-02 11:16 | MR2510/0020 | Daily | 132KV_132kV Rampur Naikin - Beohari Ckt | 132KV_RAMPUR NAIKEN | NON-OCCM-MP | OPGW Work. | 03-10-2025 07:00:00 | 30-10-2025 19:00:00 | G.L Sahu | 9425805102 | data availability confirmation required from communication
20 | 2025-10-02 11:14 | MR2510/0019 | Daily | 132KV_132kV Rewa - jhinna | 220KV_REWA | NON-OCCM-MP | OPGW Work. | 03-10-2025 07:00:00 | 30-10-2025 19:00:00 | G.L Sahu | 9425805102 | data availability confirmation required from communication
21 | 2025-10-03 13:41 | MR2510/0062 |  | 132KV_132Kv Sagar-Banda Line (Radial feeder) | 400KV_SAGAR | NON-OCCM-MP | Line maintenance work | 04-10-2025 10:00:00 | 04-10-2025 18:00:00 | J.P. Asati | 9424445533 | ok
22 | 2025-10-03 14:36 | MR2510/0068 |  | 220KV_160 mva x- mer 220/132 kv bbl | 400KV_SAGAR | NON-OCCM-MP | postmansoon maintenance work | 04-10-2025 09:00:00 | 04-10-2025 17:00:00 | srajan sisodiya | 7879960164 | ok
23 | 2025-10-03 15:59 | MR2510/0075 |  | 132KV_132 KV Shahpura-Shrinagar DP Line | 132KV_SHAHPURA | NON-OCCM-MP | Flashover Disc replacement work at loc.No.182/R-Ph | 04-10-2025 10:00:00 | 04-10-2025 18:00:00 | Ashish Kumar | 9425805935 | ok
24 | 2025-10-03 14:11 | MR2510/0064 |  | 400KV_400KV Chhegaon-I for PMU commissioning work | 400KV_SINGHAJI TPS | NON-OCCM-MP | 400KV Chhegaon-I PMU commissioning work | 04-10-2025 10:00:00 | 04-10-2025 18:00:00 | Deepak Sharma | 8005696855 | ok, through sub ld
25 | 2025-10-03 12:21 | MR2510/0058 |  | 132KV_132KV Ashta â¿¿ Sonkatchh Line | 132KV_SONKATCH | NON-OCCM-MP | Balance work of 02 No Conductor & 01 No | 04-10-2025 09:00:00 | 04-10-2025 17:00:00 | A.R.KANEL | 9425805217 | sub ld
26 | 2025-09-02 14:10 | MR2509/0043 | Continuous | 220KV_160 MVA NGEF | 220KV_UJJAIN | NON-OCCM-MP | X-MER REPLACEMENT WORK BY NEW 160 MAV XMER | 03-09-2025 09:00:00 | 03-11-2025 18:00:00 | B.C JOSHI | 7587951137 | Continuous
27 | 2025-09-02 14:10 |  |  | 132KV-VSTPS-WAIDHAN-1 |  | OCCM-WR | Annual Bay Maitenanace & Testing/ CRP replacement | 04-Oct-2025 | 08:08 | 11-Oct-2025 | 18:00 | real time
28 | 2025-09-02 14:10 |  |  | 400KV-INDORE-UJJAIN-1 |  | OCCM-WR | FOR LINE MAINTENANCE WORK i.e. CLEANING OF DISC INSULATORS DURING LINE PATROLLING , REPLACEMENT OF FLASHOVERED DISC INSULATORS, TREE BRANCH CUTTING ETC AT VARIOUS TOWER LOCATIONS | 04-Oct-2025 | 08:00 | 04-Oct-2025 | 18:00 | real time
29 | 2025-09-02 14:10 |  |  | 220KV-AJAYGARH-SATNA-1 |  | OCCM-WR | FOR LINE MAINTENANCE WORK i.e. CLEANING OF DISC INSULATORS DURING LINE PATROLLING , REPLACEMENT OF FLASHOVERED DISC INSULATORS, TREE BRANCH CUTTING ETC AT VARIOUS TOWER LOCATIONS | 04-Oct-2025 | 10:00 | 04-Oct-2025 | 17:00 | real time
S/I , SLDC MPPTCL JABALPUR