## Sheet0
STATE LOAD DESPATCH CENTRE Madhya Pradesh Power Transmission Company Limited, Jabalpur
From Date: | 2025-09-17
Control Area : | ALL | Circle : | ALL
S.NO. | APPLICATION DATE | REQ_ID | REQ TYPE | ELEMENT | SUBSTATION | CATEGORY TYPE | REASON FOR SHUT DOWN | PROPOSED START DATE & TIME | PROPOSED STOP DATE & TIME | Availing Officer Name & Mob. No. |  | REMARK
1 | 2025-08-25 15:12 | MR2508/0327 | Daily | 220KV_220KV Anuppur Kotmikala ckt-I | 220KV_ANUPPUR | NON-OCCM-MP | Low Ground clearance maintenance work at loc. 371- | 09-09-2025 08:00:00 | 17-09-2025 18:00:00 | Jitendra Tiwari | 9425805298 | DEFERRED
2 | 2025-09-12 15:03 | MR2509/0290 | Daily | 220KV_220 KV Anuppur- Kotmikala ckt-II | 220KV_ANUPPUR | NON-OCCM-MP | Resagging work at loc. 464-475 | 16-09-2025 08:00:00 | 17-09-2025 18:00:00 | Jitendra Tiwari | 9425805298 | OK
3 | 2025-09-16 13:13 | MR2509/0362 |  | 220KV_220 KV Bina-Borl Ckt-2 | 400KV_BINA4 | NON-OCCM-MP | for energy meter replacement work at their yard | 17-09-2025 14:00:00 | 17-09-2025 16:00:00 | Sanjay Singh Thakur | 9425806936 | OK PRIOR TO CHARGING ABT CONSENT REQUIRED, METER MASTER DATA TO BE SUBMITTED, THROUGH SUB LD
4 | 2025-09-16 13:10 | MR2509/0361 |  | 220KV_220 KV Bina-Borl Ckt-1 | 400KV_BINA4 | NON-OCCM-MP | for energy meter replacement work at their yard | 17-09-2025 11:00:00 | 17-09-2025 13:00:00 | Sanjay Singh Thakur | 9425806936 | OK PRIOR TO CHARGING ABT CONSENT REQUIRED, METER MASTER DATA TO BE SUBMITTED, THROUGH SUB LD
5 | 2025-09-14 13:00 | MR2509/0312 | Daily | 132KV_132 kV Shahdol-Birsinghpur Circuit I | 220KV_BIRSINGHPUR | NON-OCCM-MP | For replacement of damaged OPGW | 15-09-2025 08:00:00 | 20-09-2025 18:00:00 | Jitendra Tiwari | 9425805298 | OK FOR 15.09.2025 DAILY BASIS SD
6 | 2025-09-14 13:01 | MR2509/0313 | Daily | 132KV_132 kV Shahdol-Dindori Circuit II | 132KV_DINDORI | NON-OCCM-MP | For replacement of damaged OPGW | 15-09-2025 08:00:00 | 20-09-2025 18:00:00 | Jitendra Tiwari | 9425805298 | OK FOR 15.09.2025 DAILY BASIS SD
7 | 2025-09-07 13:02 | MR2509/0161 | Daily | 220KV_220KV North Zone- Hatuniya(PGCIL) Ckt.-2 | 220KV_INDORE NORTH | NON-OCCM-MP | Replacement existing of 24 Fibre OPGW by 48 Fibre | 11-09-2025 07:00:00 | 30-09-2025 19:00:00 | A.R.KANEL | 9425805217 | OK LINE TO BE IN SERVICE
8 | 2025-09-07 12:51 | MR2509/0159 | Daily | 132KV_132KV North Zone- Jaitpura Line | 220KV_INDORE-II (JETPURA) | NON-OCCM-MP | Replacement existing of 24 Fibre OPGW by 48 Fibre | 11-09-2025 07:00:00 | 30-09-2025 19:00:00 | A.R.KANEL | 9425805217 | SUB LD
9 | 2025-09-07 12:45 | MR2509/0158 | Daily | 220KV_220KV North Zone- Hatuniya(PGCIL) Ckt.-1 | 220KV_INDORE-NZ | NON-OCCM-MP | Replacement existing of 24 Fibre OPGW by 48 Fibre | 11-09-2025 07:00:00 | 30-09-2025 19:00:00 | A.R.KANEL | 9425805217 | OK LINE TO BE IN SERVICE
10 | 2025-09-02 18:32 | MR2509/0063 | Daily | 220KV_220KV North Zone- Hatuniya(PGCIL) Ckt.-1& ckt-2 | 220KV_INDORE-NZ | NON-OCCM-MP | Replacement existing of 24 Fibre OPGW by 48 Fibre | 05-09-2025 07:00:00 | 25-09-2025 19:00:00 | A.R.KANEL | 9425805217 | RESCHEDULED FRO 11.09.2025 TO 30.09.2025
11 | 2025-09-15 13:47 | MR2509/0335 | Continuous | 132KV_132 kv Katni-sleemnabad ckt 2nd line | 132KV_KATNI | NON-OCCM-MP | Modification shifting work for Nhai | 16-09-2025 12:00:00 | 17-09-2025 12:00:00 | pankaj yadav | 9406713326 | SD NOT AVAILED
12 | 2025-09-16 14:49 | MR2509/0365 | Continuous | 132KV_132 kv katni sleemanbad line 2nd ckt | 132KV_KATNI | NON-OCCM-MP | maintence work, Modification shifting work for Nhai | 17-09-2025 09:00:00 | 18-09-2025 18:00:00 | pankaj yadav | 9406713326 | OK, EI APPROVAL TO BE PROVIDED PRIOR TO CHARGING
13 | 2025-09-07 12:39 | MR2509/0157 | Daily | 132KV_132KV North Zone â¿¿ Niranjanpur Line. | 132KV_NIRANJANPUR | NON-OCCM-MP | Replacement existing of 24 Fibre OPGW by 48 Fibre | 11-09-2025 07:00:00 | 30-09-2025 19:00:00 | A.R.KANEL | 9425805217 | SUB LD\
14 | 2025-09-07 12:57 | MR2509/0160 | Daily | 132KV_132KV Niranjanpur - Jaitpura Line | 132KV_NIRANJANPUR | NON-OCCM-MP | Replacement existing of 24 Fibre OPGW by 48 Fibre | 11-09-2025 07:00:00 | 30-09-2025 19:00:00 | A.R.KANEL | 9425805217 | SUB LD
15 | 2025-09-02 18:36 | MR2509/0064 | Daily | 132KV_132KV North Zone â¿¿ Niranjanpur Line.&132KV Niranjanpur - Jaitpura Line &132KV North Zone- Jaitpura Line | 132KV_NIRANJANPUR | NON-OCCM-MP | Replacement existing of 24 Fibre OPGW by 48 Fibre | 05-09-2025 07:00:00 | 25-09-2025 19:00:00 | A.R.KANEL | 9425805217 | SUB LD
16 | 2025-09-16 15:11 | MR2509/0366 |  | 132KV_132kV Rajmilan - Jankapur Ckt | 132KV_RAJMILAN | NON-OCCM-MP | Disc Replacement work | 17-09-2025 08:30:00 | 17-09-2025 17:00:00 | G.L Sahu | 9425805102 | OK, Janakpur supply to be maintained through Anuppur.
17 | 2025-09-02 14:10 | MR2509/0042 | Continuous | 220KV_160 MVA NGEF | 220KV_UJJAIN | NON-OCCM-MP | X-MER REPLACEMENT WORK BY NEW 160 MAV XMER | 03-09-2025 09:00:00 | 03-11-2025 18:00:00 | B.C JOSHI | 7587951137 | OK, FTC TO BE SUBMITTED
18 | 2025-09-01 16:04 | MR2509/0027 | Continuous | 132KV_132 KV VINOBA BHAVE TAPE LINE | 132KV_VINOBA BHAVE | NON-OCCM-MP | UPGRADATION OF 132 KV VINOBA BHAVE LINE | 02-09-2025 08:00:00 | 25-09-2025 18:00:00 | RAJESH TIWARI | 7898239595 | CONTINUE
19 |  |  |  | SATPURA - 400KV - BUS 2 |  | POWERGRID_WR2 | For replacemnet of Bus-2 PG isolator under ADD CAP at MPGENCO (Simultaneous outage of 400KV-SATPURA-ITARSI-1 is required) | 16-2025-09 | 09-00 | 19-2025-09 | 20-00 | CONTINUE ,SLDC MP Consent to be taken. all elements to be in service with Bus-1. No other element shall be affected. In case of N-1 contigencies load to be managed by SLDC MP. care to be taken.400KV-SATPURA-ITARSI-1 outage is also aproved
20 |  |  |  | 400KV-SATPURA-ITARSI-1 |  | POWERGRID_WR2 | For replacemnet of Bus-2 PG isolator under ADD CAP at MPGENCO (Simultaneous outage of 400kV Bus-1 is required at Sarni S/S of MPGENCO) And CT Replacement of 400KV-SATPURA-ITARSI-1 under ADD CAP at MPGENCO | 16-2025-09 | 09-00 | 19-2025-09 | 20-00 | CONTINUE ,SLDC MP Consent to be taken.400kV SATPURA-INDIRASAGAR-T1 (Sensitivity of 34%) and All other lines at Satpura to be in service with AR enabled. SLDC MP to be informed.
21 |  |  |  | 220KV-GWALIOR-MAHALGAON-2 |  | MP_SLDC | FOR BAY MAINTENANCE & TESTING WORK AT SUBSTASTION, REPLACEMENT OF DAMAGED CLAMPS/JUMPERS ETC. | 17-2025-09 | 09-00 | 17-2025-09 | 17-00 | OK THROUGH SUB LD, All other lines at Mahalgaon to be in service with AR enabled. WR2 to be informed. load to be managed by SLDC MP
22 |  |  |  | 220KV-ANNUPUR-KOTMIKALA-2 |  | MP_SLDC | For Re-sagging work due to Low Ground clearance maintenance work at loc. 464-475. | 17-2025-09 | 09-00 | 17-2025-09 | 20-00 | ok, All other lines at Annuppur/Kotmikala to be in service. SLDC CG to be informed. Load to be managed by SLDC MP/CG.
23 |  |  |  | 400KV/220KV JABALPUR-ICT-2 |  | MP_SLDC | FOR BAY MAINTENANCE & TESTING WORK AT SUBSTASTION, REPLACEMENT OF DAMAGED CLAMPS/JUMPERS ETC. | 16-2025-09 | 09-00 | 17-2025-09 | 17-00 | CONTINUE , ICT-1 (sensitivity-28%),3 (sensitivity-44%)to be in service with complete dia. SLDC MP to be informed. Load to be managed by SLDC MP In case of contingency.
24 |  |  |  | 220KV-INDORE-INDORE NORTH ZONE-1 |  | MP_SLDC | PEPLACEMENT OF EXISTING 24FIBRE OPGW WITH48 FIBRE OPGW. DATA IS DIVERTED, ONLINE WORK PERMIT, AUTO TO NON AUTO | 17-2025-09 | 07-00 | 17-2025-09 | 24-00 | OK LINE TO BE IN SERVICE
25 |  |  |  | 220KV-INDORE-INDORE NORTH ZONE-2 |  | MP_SLDC | PEPLACEMENT OF EXISTING 24FIBRE OPGW WITH48 FIBRE OPGW. DATA IS DIVERTED, ONLINE WORK PERMIT, AUTO TO NON AUTO | 17-2025-09 | 07-00 | 17-2025-09 | 20-00 | OK LINE TO BE IN SERVICE ,