## Sheet0
STATE LOAD DESPATCH CENTRE Madhya Pradesh Power Transmission Company Limited, Jabalpur
From Date: | 2025-07-15
Control Area : | ALL | Circle : | ALL
S.NO. | APPLICATION DATE | REQ_ID | REQ TYPE | ELEMENT | SUBSTATION | CATEGORY TYPE | REASON FOR SHUT DOWN | PROPOSED START DATE & TIME | PROPOSED STOP DATE & TIME | Availing Officer Name & Mob. No. |  | REMARK
1 | 2025-06-30 16:24 | MR2506/0639 | Daily | 220KV_220 KV MUGALIYACHAP ASHTA | 400KV_ASHTA4 | NON-OCCM-MP | HOT LINE PERMIT | 01-07-2025 09:00:00 | 20-07-2025 19:00:00 | NITIN RESHWAL | 9425804890 | ok, line to be in service
2 | 2025-06-30 16:26 | MR2506/0640 | Daily | 220KV_220 KV BAIRAGARH-ASHTA | 220KV_BAIRAGARH | NON-OCCM-MP | HOT LINE PERMIT | 01-07-2025 09:00:00 | 20-07-2025 19:00:00 | NITIN RESHWAL | 9425804890 | ok, line to be in service
3 | 2025-06-30 16:13 | MR2506/0635 | Daily | 220KV_220 BHOPAL-BAIRAGARH CKT-3 | 220KV_BAIRAGARH | NON-OCCM-MP | HOT LINE PERMIT | 01-07-2025 09:00:00 | 20-07-2025 19:00:00 | NITIN RESHWAL | 9425804890 | ok, line to be in service
4 | 2025-07-02 18:54 | MR2507/0044 | Daily | 132KV_132kV Rewa - Bansagar Lilo Beohari -Lilo Jhinna | 132KV_BEOHARI | NON-OCCM-MP | OPGW Hot Line | 03-07-2025 07:00:00 | 30-07-2025 19:00:00 | G.L Sahu | 9425805102 | ok, line to be in service
5 | 2025-07-14 11:10 | MR2507/0184 |  | 220KV_220KV MAIN BUS -2 | 220KV_BIRSINGHPUR | NON-OCCM-MP | BUS TIE MAIN BUS -2 ISOLATOR Y PHASE JUMPER REPLAC | 15-07-2025 10:00:00 | 15-07-2025 18:00:00 | TOSHAN SINGH | 9425809482 | ok, no other element shall be out
6 | 2025-07-12 09:15 | MR2507/0160 |  | 220KV_220KV BUDHNI-PGCIL(ITARSI) CKT - 1ST | 220KV_BUDHNI | NON-OCCM-MP | RELAY INSTALLATION & ISOLATOR ALIGMENT WORK | 15-07-2025 11:00:00 | 15-07-2025 17:00:00 | SHRI SATYA PAL SINGH TOMAR | 9425801629 | ok, through sub ld
7 | 2025-07-12 13:24 | MR2507/0165 | Daily | 400KV_125 MVAr SHUNT REACTOR | 400KV_INDIRASAGAR | NON-OCCM-WR | ANNUAL MAINTENANCE | 15-07-2025 10:00:00 | 17-07-2025 17:00:00 | SHRI VINAI MISHRA | 9575074321 | kindly confirm why the reactor outage is planned when it is most needed( during low demand period) ?
8 | 2025-06-23 17:09 | MR2506/0482 | Daily | 220KV_220 KV South Zone - Jaitpura Line | 220KV_INDORE-II (JETPURA) | NON-OCCM-MP | Existing 24 Fibre OPGW Wire by 48 Fibre OPGW work | 24-06-2025 07:00:00 | 15-07-2025 19:00:00 | A.R. KANEL | 9425805217 | ok, line to be in service
9 | 2025-06-23 17:04 | MR2506/0481 | Daily | 220KV_220KV Indore (400KV) - Mangliya line | 400KV_INDORE4 | NON-OCCM-MP | Existing 24 Fibre OPGW Wire by 48 Fibre OPGW work | 24-06-2025 07:00:00 | 15-07-2025 19:00:00 | A.R.KANEL | 9425805217 | ok, line to be in service
10 | 2025-07-12 13:33 | MR2507/0167 |  | 220KV_220KV Itarsi Sarni.-3 CT | 220KV_ITARSI | NON-OCCM-MP | R&Y Phase CT Replacement work | 15-07-2025 09:00:00 | 15-07-2025 18:00:00 | J.D.Khoria | 9425804975 | ok, through sub ld
11 | 2024-11-20 16:49 | MR2411/0436 | Continuous | 400KV_400 KV KATNI-DAMOH LINE | 400KV_KATNI4 | NON-OCCM-WR | TOWER STRENGTHENING WORK | 14-07-2025 09:00:00 | 19-07-2025 18:00:00 | MANOJ KUMAR TIWARI | 9425804993 | Continuous
12 | 2024-11-20 16:54 | MR2411/0437 | Continuous | 220KV_220 KV KATNI-DAMOH LINE | 400KV_KATNI4 | NON-OCCM-MP | TOWER STRENGTHENING WORK | 14-07-2025 09:00:00 | 19-07-2025 18:00:00 | MANOJ KUMAR TIWARI | 9425804993 | Continuous
13 | 2025-07-12 10:50 | MR2507/0161 | Continuous | 132KV_132 KV Khurai-Sagar Ckt | 132KV_KHURAI | NON-OCCM-MP | Extension of continous Sd for Modification work | 12-07-2025 07:00:00 | 18-07-2025 18:00:00 | Sanjay Singh Thakur | 9425806936 | Continuous
14 | 2025-06-30 16:20 | MR2506/0638 | Daily | 220KV_220 KV BHOPAL-MUGALIYACHAP | 220KV_MUGALIYACHAAP | NON-OCCM-MP | HOT LINE PERMIT | 01-07-2025 09:00:00 | 20-07-2025 19:00:00 | NITIN RESHWAL | 9425804890 | ok, line to be in service
15 | 2025-07-05 17:07 | MR2507/0079 | Daily | 132KV_132 kV Nepa - Pipalpani MPPTCL Line | 220KV_NEPANAGAR | NON-OCCM-WR | Hotline Work Insatallation of OPGW | 11-07-2025 08:00:00 | 30-07-2025 18:00:00 | C.H.Namdev | 9425802377 | sub ld
16 | 2025-07-05 16:59 | MR2507/0078 | Daily | 132KV_132 kV Nepa - Dharni (MSPTCL) LIne | 220KV_NEPANAGAR | NON-OCCM-WR | Hotline Work For Installation of OPGW | 08:00:00 | 30-07-2025 18:00:00 | C.H.Namdev | 9425802377 | ok, line to be in service
17 | 2025-07-11 16:34 | MR2507/0155 | Daily | 220KV_Main BUSâ¿¿A and Bus Coupler | 220KV_OMKARESHWAR | NON-OCCM-MP | Annual Maintenance | 15-07-2025 09:00:00 | 16-07-2025 18:00:00 | PANKAJ SHARMA | 7898703187 | Deffered due to high OSP generation
18 | 2025-07-11 16:30 | MR2507/0154 | Daily | 220KV_Omkareshwar-Nimrani Line#1(Tap Barwaha) | 220KV_OMKARESHWAR | NON-OCCM-MP | Annual Maintenance | 14-07-2025 09:00:00 | 17-07-2025 18:00:00 | PANKAJ SHARMA | 7898703187 | Deffered due to high OSP generation
19 |  |  |  | 160 MVA X-MER | 220 KV MAHALGAON GWALIOR |  | KAMISNING OF ONLINE DRY OUT SYSTEM | 13:00 | 17:00 |  |  | ok, through sub ld
20 |  |  |  | 33 KV MAIN BUS AT 220 KV S/S SEONI | 220 KV SEONI |  | NEWLY CONSTUCTD BUS COUPLER BY JUMPER TO CONNECT 33 KV MAIN BUS | 8:00 | 10:00 |  |  | OK
21 |  |  |  | 400 KV INDORE ISP II LINE | 400 KV INDORE |  | 400 KV ISOLATOR OF NEW 50 MVAR REACTOR AT 400 KV S/S AT INDORE | 8:00 | 15:00 |  |  | OK MAX. 5 - 6 M/CS ALLOWED DURING S/D PRIOED
22 |  |  |  | 160 MVA X-MER MAKE BHEL | 220 KV SHUJALPUR |  | IR VALUE MEASURMENT WORK | 9:00 | 17:00 |  |  | ok, through sub ld
23 |  |  |  | 400 KV TVC | 400 KV PITHAMPUR |  | REALY TESTING & BAY MAINTANANCE WORK | 11:00 | 18:00 |  |  | ok, through sub ld
24 |  |  |  | 132 KV SIDHI MAUGANJ CKT - II | 220KV SIDHI |  | LINE MAINT. WORK | 9:30 | 16:00 |  |  | OK
25 |  |  |  | 132 KV SEONI LAKHNADON SC FEEDER | 220 KV SEONI |  | REPLACEMENT OF FLASHOVER DISC INSULATOR | 10:00 | 17:00 |  |  | OK
26 |  |  |  | 20 MVA CGL X-MER | 132 WAIDHAN |  | REALY PENAL REPLACEMENT WORK | 9:00 | 17:00 |  |  | OK
27 |  |  |  | 220 KV MAIN BUS - I | 220 KV PITHAMPUR SECTOR III |  | 220 KV DHAR FEEDER MAIN BUS - I ISOLATORS REP. WORK | 10:00 | 17:00 |  |  | NOT CLEAR
28 |  |  |  | 132 KV SAGAR - IC - I CKT | MPPTCL HQ DAMOH |  | WORK INSTALLATION OF OPGW | 10:00 | 17:00 |  |  | REAL TIME , O&M SHALL BE INFORM
29 |  |  |  | 132 KV Main bus section-II | 220 KV S/s Jaora |  | for carrying out 132/33KV 50 mva X mer Make BHEL main Bus isolator jumper open work from main bus. | 10:00 | 13:00 |  |  | ok, through sub ld, IF LOAD IS MANAGEBLE IN 132 KV NETWORK
30 |  |  |  | 220 KV MAIN BUS - II | 220 KV SUWASRA ( MANDSAUR) |  | DIFECTIVE ISOLATOR ALIGNMENT OF VARIOUS FEEDER | 11:00 | 2:00:00 PM ( UP TO 16-07-25 |  |  | ok, through sub ld
31 |  | 253330 |  | 220KV-INDORE-UJJAIN-2 | 220 | MP_SLDC | FOR LINE MAINTENANCE WORK | 15-Jul-2025 | 08:00 | 15-Jul-2025 | 18:00 | real time
32 |  | 253331 |  | 220KV-MORENA-MORENA-MP-1 | 220 | MP_SLDC | FOR LINE MAINTENANCE WORK | 15-Jul-2025 | 09:00 | 15-Jul-2025 | 17:00 | ok, through sub ld
33 |  | 253332 |  | 220KV-SEONI-PG-CHINDWARA-1 | 220 | MP_SLDC | FOR LINE MAINTENANCE WORK | 15-Jul-2025 | 09:00 | 15-Jul-2025 | 18:00 | real time
34 |  | 258856 |  | 220KV-ITARSI-BUDNI-1 | 220 | MP_SLDC | FOR SECOND PROTECTION RELAY INSTALLATION WORK AND ISOALTOR ALIGNMENT WORK | 15-Jul-2025 | 11:00 | 15-Jul-2025 | 17:59 | ok, through sub ld
35 |  | 253296 |  | 400KV-BHOPAL-MP-BINA-MP-1 | 400 | MP_SLDC | FOR BAY MAINTENANCE & TESTING WORK | 15-Jul-2025 | 09:00 | 15-Jul-2025 | 18:00 | real time
36 |  | 252953 |  | 400KV-KORADI-SATPURA-1 | 400 | POWERGRID_WR2 | For replacemnet of Bus-1 PG isolator under ADD CAP at MPGENCO (Simultaneous outage of 400kV Bus-1 is required at Sarni S/S of MPGENCO) | 15-Jul-2025 | 09:00 | 18-Jul-2025 | 20:00 | ok
37 |  | 252952 |  | SATPURA - 400KV - BUS 1 | 400 | POWERGRID_WR2 | For replacemnet of Bus-1 PG isolator under ADD CAP at MPGENCO (Simultaneous outage of 400KV-SATPURA-KORADI-1 is required) | 15-Jul-2025 | 09:00 | 18-Jul-2025 | 20:00 | ok
38 |  | 257831 |  | 132KV-DHARNI-NEPANAGAR-1 | 132 | MP_SLDC | A/R off required for OPGW installation work of 24/48 core OPGW by replacing E/W for implementation of OPGW based reliable communication scheme | 15-Jul-2025 | 08:00 | 15-Jul-2025 | 17:59 | ok

## Sheet1
13:00 | 17:00